{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":39,"n_cols":8,"rows_kept":39,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","AZQS-BY1 UK"]
[]
[]
[]
[]
["","","","","","AZQS100B7Y1B UK","AZQS125B7Y1B UK","AZQS140B7Y1B UK"]
["Sound pressure level","Heating","","Nom.","dBA","57","58","54"]
["","Cooling","","Nom.","dBA","53","54","53"]
["","Night quiet mode","","Level 1","dBA","49","49","49"]
["Standard Accessories","Tie-wraps","","","","2","2","2"]
["","Installation manual","","","","1","1","1"]
["Refrigerant","Charge","","","TCO2Eq","6.1","6.1","8.4"]
["","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","2.9","2.9","4.0"]
["","Type","","","","R-410A","R-410A","R-410A"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","9.52"]
["","Piping length","OU - IU","Max.","m","30 (7)","30 (7)","30 (7)"]
["","","System","Chargeless","m","30","30","30"]
["","","","Equivalent","m","40","40","40"]
["","Gas","","OD","mm","15.9","15.9","15.9"]
["","Level difference","IU - IU","Max.","m","0.5","0.5","0.5"]
["","","IU - OU","Max.","m","30.0","30.0","30.0"]
["","Additional refrigerant charge","","","kg/m","See installation manual","See installation manual","See installation manual"]
["Sound power level","Cooling","","","dBA","70","71","70"]
["Dimensions","Unit","","Width","mm","940","940","940"]
["","","","Depth","mm","320","320","320"]
["","","","Height","mm","990","990","1,430"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Weight","Unit","","","kg","82","82","101"]
["Power supply","Phase","","","","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415"]
["Notes","","","","","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC"]
["","","","","","(2) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase","(2) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase","(2) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase"]
["","","","","","(3) - See separate drawing for electrical data","(3) - See separate drawing for electrical data","(3) - See separate drawing for electrical data"]
["","","","","","(4) - Contains fluorinated greenhouse gases","(4) - Contains fluorinated greenhouse gases","(4) - Contains fluorinated greenhouse gases"]
["","","","","","(5) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified","(5) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified","(5) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified"]
["","","","","","(6) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified","(6) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified","(6) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified"]
["","","","","","(7) - For details regarding your combination of oudoor and indoor unit, refer to the technical databook","(7) - For details regarding your combination of oudoor and indoor unit, refer to the technical databook","(7) - For details regarding your combination of oudoor and indoor unit, refer to the technical databook"]