{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":10,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EKHVX-BB"]
[]
[]
[]
[]
["","","","","EKHVX008BB6V3","EKHVX008BB6WN","EKHVX008BB9WN","EKHVX016BB6WN","EKHVX016BB9WN","EKHVX016BB6V3"]
["Sound pressure level","Medium speed","0 ESP","dBA","28 (9)","28 (9)","28 (9)","28 (15)","28 (15)","28 (15)"]
["Sound power level","Medium speed","0 ESP","dBA","42","42","42","46","46","46"]
["Dimensions","Unit","Width","mm","600","600","600","600","600","600"]
["","","Depth","mm","695","695","695","695","695","695"]
["","","Height","mm","705","705","705","705","705","705"]
["Casing","Material","","","Precoated sheet metal","Precoated sheet metal","Precoated sheet metal","Precoated sheet metal","Precoated sheet metal","Precoated sheet metal"]
["","Colour","","","Metallic grey","Metallic grey","Metallic grey","Metallic grey","Metallic grey","Metallic grey"]
["Weight","Unit","","kg","65","65","65","67","67","67"]
["Wiring connections","For connection with user interface","Remark","","Cable section minimum 0.75mm², maximum length 500m","Cable section minimum 0.75mm², maximum length 500m","Cable section minimum 0.75mm², maximum length 500m","Cable section minimum 0.75mm², maximum length 500m","Cable section minimum 0.75mm², maximum length 500m","Cable section minimum 0.75mm², maximum length 500m"]
["","","Quantity","","2","2","2","2","2","2"]
["Electric heater","Current back-up heater","Running current","A","26 (18)","8.7 (19)","13 (20)","8.7 (25)","13 (26)","26 (24)"]
["","Power supply","Frequency","Hz","50","50","50"]
["","","Voltage","V","230","400","400","400","400","230"]
["","","Phase","","1~","3~","3~","3~","3~","1~"]
["Notes","","","","(1) - In combination with ERHQ006BAV3","(1) - In combination with ERHQ006BAV3","(1) - In combination with ERHQ006BAV3","(1) - In combination with ERHQ011BAV3","(1) - In combination with ERHQ011BAV3","(1) - In combination with ERHQ011BAV3"]
["","","","","(2) - In combination with ERLQ006BAV3","(2) - In combination with ERLQ006BAV3","(2) - In combination with ERLQ006BAV3","(2) - In combination with ERLQ011BAV3","(2) - In combination with ERLQ011BAV3","(2) - In combination with ERLQ011BAV3"]
["","","","","(3) - In combination with ERHQ007BAV3","(3) - In combination with ERHQ007BAV3","(3) - In combination with ERHQ007BAV3","(3) - In combination with ERHQ011BAW1","(3) - In combination with ERHQ011BAW1","(3) - In combination with ERHQ011BAW1"]
["","","","","(4) - In combination with ERLQ007BAV3","(4) - In combination with ERLQ007BAV3","(4) - In combination with ERLQ007BAV3","(4) - In combination with ERLQ011BAW1","(4) - In combination with ERLQ011BAW1","(4) - In combination with ERLQ011BAW1"]
["","","","","(5) - In combination with ERHQ008BAV3","(5) - In combination with ERHQ008BAV3","(5) - In combination with ERHQ008BAV3","(5) - In combination with ERHQ014BAV3","(5) - In combination with ERHQ014BAV3","(5) - In combination with ERHQ014BAV3"]
["","","","","(6) - In combination with ERLQ008BAV3","(6) - In combination with ERLQ008BAV3","(6) - In combination with ERLQ008BAV3","(6) - In combination with ERLQ014BAV3","(6) - In combination with ERLQ014BAV3","(6) - In combination with ERLQ014BAV3"]
["","","","","(7) - Tamb 35°C - LWE 7°C (Dt=5°C) at high speed","(7) - Tamb 35°C - LWE 7°C (Dt=5°C) at high speed","(7) - Tamb 35°C - LWE 7°C (Dt=5°C) at high speed","(7) - In combination with ERHQ014BAW1","(7) - In combination with ERHQ014BAW1","(7) - In combination with ERHQ014BAW1"]
["","","","","(8) - DB/WB 7°C/6°C - LWC 35°C (Dt=5°C) at high speed","(8) - DB/WB 7°C/6°C - LWC 35°C (Dt=5°C) at high speed","(8) - DB/WB 7°C/6°C - LWC 35°C (Dt=5°C) at high speed","(8) - In combination with ERLQ014BAW1","(8) - In combination with ERLQ014BAW1","(8) - In combination with ERLQ014BAW1"]
["","","","","(9) - The sound pressure level is measured via a microphone at a 1m distance from the unit. It is a relative value, depending on the distance and acoustic environment.","(9) - The sound pressure level is measured via a microphone at a 1m distance from the unit. It is a relative value, depending on the distance and acoustic environment.","(9) - The sound pressure level is measured via a microphone at a 1m distance from the unit. It is a relative value, depending on the distance and acoustic environment.","(9) - In combination with ERHQ016BAV3","(9) - In combination with ERHQ016BAV3","(9) - In combination with ERHQ016BAV3"]
["","","","","(10) - The sound pressure level mentioned is valid for pump medium speed - 0 ESP / medium speed - nominal flow / high speed - nominal flow","(10) - The sound pressure level mentioned is valid for pump medium speed - 0 ESP / medium speed - nominal flow / high speed - nominal flow","(10) - The sound pressure level mentioned is valid for pump medium speed - 0 ESP / medium speed - nominal flow / high speed - nominal flow","(10) - In combination with ERLQ016BAV3","(10) - In combination with ERLQ016BAV3","(10) - In combination with ERLQ016BAV3"]
["","","","","(11) - 15°C-25°C: BUH only, no heat pump operation = during commissioning","(11) - 15°C-25°C: BUH only, no heat pump operation = during commissioning","(11) - 15°C-25°C: BUH only, no heat pump operation = during commissioning","(11) - In combination with ERHQ016BAW1","(11) - In combination with ERHQ016BAW1","(11) - In combination with ERHQ016BAW1"]
["","","","","(12) - Including piping + PHE + back-up heater; excluding expansion vessel","(12) - Including piping + PHE + back-up heater; excluding expansion vessel","(12) - Including piping + PHE + back-up heater; excluding expansion vessel","(12) - In combination with ERLQ016BAW1","(12) - In combination with ERLQ016BAW1","(12) - In combination with ERLQ016BAW1"]
["","","","","(13) - See separate drawing for operation range","(13) - See separate drawing for operation range","(13) - See separate drawing for operation range","(13) - Tamb 35°C - LWE 7°C (Dt=5°C) at high speed","(13) - Tamb 35°C - LWE 7°C (Dt=5°C) at high speed","(13) - Tamb 35°C - LWE 7°C (Dt=5°C) at high speed"]
["","","","","(14) - Operation range: only with optional *KHTS* tank. Water temperatures higher than 50°C are with BUH only. More details, see operation range drawnig","(14) - Operation range: only with optional *KHTS* tank. Water temperatures higher than 50°C are with BUH only. More details, see operation range drawnig","(14) - Operation range: only with optional *KHTS* tank. Water temperatures higher than 50°C are with BUH only. More details, see operation range drawnig","(14) - DB/WB 7°C/6°C - LWC 35°C (Dt=5°C) at high speed","(14) - DB/WB 7°C/6°C - LWC 35°C (Dt=5°C) at high speed","(14) - DB/WB 7°C/6°C - LWC 35°C (Dt=5°C) at high speed"]
["","","","","(15) - Above mentioned power supply of the hydrobox is for the backup heater only. The switch box and the pump of the hydrobox are supplied via the outdoor unit.","(15) - Above mentioned power supply of the hydrobox is for the backup heater only. The switch box and the pump of the hydrobox are supplied via the outdoor unit.","(15) - Above mentioned power supply of the hydrobox is for the backup heater only. The switch box and the pump of the hydrobox are supplied via the outdoor unit.","(15) - The sound pressure level is measured via a microphone at a 1m distance from the unit. It is a relative value, depending on the distance and acoustic environment.","(15) - The sound pressure level is measured via a microphone at a 1m distance from the unit. It is a relative value, depending on the distance and acoustic environment.","(15) - The sound pressure level is measured via a microphone at a 1m distance from the unit. It is a relative value, depending on the distance and acoustic environment."]
["","","","","(16) - Electric heater has 2 capacity steps","(16) - Electric heater has 2 capacity steps","(16) - Electric heater has 2 capacity steps","(16) - The sound pressure level mentioned is valid for pump medium speed - 0 ESP / medium speed - nominal flow / high speed - nominal flow","(16) - The sound pressure level mentioned is valid for pump medium speed - 0 ESP / medium speed - nominal flow / high speed - nominal flow","(16) - The sound pressure level mentioned is valid for pump medium speed - 0 ESP / medium speed - nominal flow / high speed - nominal flow"]
["","","","","(17) - In accordance with EN/IEC 61000-3-11, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys (system impedance) ≤ Zmax","(17) - In accordance with EN/IEC 61000-3-11, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys (system impedance) ≤ Zmax","(17) - In accordance with EN/IEC 61000-3-11, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys (system impedance) ≤ Zmax","(17) - 15°C-25°C: BUH only, no heat pump operation = during commissioning","(17) - 15°C-25°C: BUH only, no heat pump operation = during commissioning","(17) - 15°C-25°C: BUH only, no heat pump operation = during commissioning"]
["","","","","(18) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 26 to 13A. Please refer to the installation manual for instructions.","(18) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 26 to 13A. Please refer to the installation manual for instructions.","(18) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 26 to 13A. Please refer to the installation manual for instructions.","(18) - Including piping + PHE + back-up heater; excluding expansion vessel","(18) - Including piping + PHE + back-up heater; excluding expansion vessel","(18) - Including piping + PHE + back-up heater; excluding expansion vessel"]
["","","","","(19) - The installer can reduce the capacity of the heater from 6 to 2kW. The current is then reduced from 8.7 to 5A. Please refer to the installation manual for instructions.","(19) - The installer can reduce the capacity of the heater from 6 to 2kW. The current is then reduced from 8.7 to 5A. Please refer to the installation manual for instructions.","(19) - The installer can reduce the capacity of the heater from 6 to 2kW. The current is then reduced from 8.7 to 5A. Please refer to the installation manual for instructions.","(19) - See operation range drawing for difference between single & three phase units","(19) - See operation range drawing for difference between single & three phase units","(19) - See operation range drawing for difference between single & three phase units"]
["","","","","(20) - The installer can reduce the capacity of the heater from 9 to 3kW. The current is then reduced from 13 to 7.5A. Please refer to the installation manual for instructions.","(20) - The installer can reduce the capacity of the heater from 9 to 3kW. The current is then reduced from 13 to 7.5A. Please refer to the installation manual for instructions.","(20) - The installer can reduce the capacity of the heater from 9 to 3kW. The current is then reduced from 13 to 7.5A. Please refer to the installation manual for instructions.","(20) - Operation range: only with optional *KHTS* tank. Water temperatures higher than 55°C are with BUH only. More details, see operation range drawnig","(20) - Operation range: only with optional *KHTS* tank. Water temperatures higher than 55°C are with BUH only. More details, see operation range drawnig","(20) - Operation range: only with optional *KHTS* tank. Water temperatures higher than 55°C are with BUH only. More details, see operation range drawnig"]
["","","","","(21) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(21) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(21) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(21) - Above mentioned power supply of the hydrobox is for the backup heater only. The switch box and the pump of the hydrobox are supplied via the outdoor unit.","(21) - Above mentioned power supply of the hydrobox is for the backup heater only. The switch box and the pump of the hydrobox are supplied via the outdoor unit.","(21) - Above mentioned power supply of the hydrobox is for the backup heater only. The switch box and the pump of the hydrobox are supplied via the outdoor unit."]
["","","","","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(22) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(22) - Optional electric heater has 2 capacity steps except for the 3V3 model which has only 1 capacity step.","(22) - Optional electric heater has 2 capacity steps except for the 3V3 model which has only 1 capacity step.","(22) - Optional electric heater has 2 capacity steps except for the 3V3 model which has only 1 capacity step."]
["","","","","","","","(23) - In accordance with EN/IEC 61000-3-11, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys (system impedance) ≤ Zmax","(23) - In accordance with EN/IEC 61000-3-11, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys (system impedance) ≤ Zmax","(23) - In accordance with EN/IEC 61000-3-11, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys (system impedance) ≤ Zmax"]
["","","","","","","","(24) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 26 to 13A. Please refer to the installation manual for instructions.","(24) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 26 to 13A. Please refer to the installation manual for instructions.","(24) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 26 to 13A. Please refer to the installation manual for instructions."]
["","","","","","","","(25) - The installer can reduce the capacity of the heater from 6 to 2kW. The current is then reduced from 8.7 to 5A. Please refer to the installation manual for instructions.","(25) - The installer can reduce the capacity of the heater from 6 to 2kW. The current is then reduced from 8.7 to 5A. Please refer to the installation manual for instructions.","(25) - The installer can reduce the capacity of the heater from 6 to 2kW. The current is then reduced from 8.7 to 5A. Please refer to the installation manual for instructions."]
["","","","","","","","(26) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 13 to 7.5A. Please refer to the installation manual for instructions.","(26) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 13 to 7.5A. Please refer to the installation manual for instructions.","(26) - The installer can reduce the capacity of the heater from 6 to 3kW. The current is then reduced from 13 to 7.5A. Please refer to the installation manual for instructions."]
["","","","","","","","(27) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(27) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(27) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A"]
["","","","","","","","(28) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(28) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(28) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]