{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":45,"n_cols":11,"rows_kept":45,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ERHQ-BV3"]
[]
[]
[]
[]
["","","","","","ERHQ006BAV3","ERHQ007BAV3","ERHQ008BAV3","ERHQ011BAV3","ERHQ014BAV3","ERHQ016BAV3"]
["Sound pressure level","Heating","","Nom.","dBA","48","48","49","49 (5)","51 (5)","53 (5)"]
["","Cooling","","Nom.","dBA","48","48","50","50 (6)","52 (6)","54 (6)"]
["Standard Accessories","Installation manual","","","","1","1","1"]
["","Drain plug","","","","1","1","1"]
["Refrigerant","Charge","","","TCO2Eq","3.5","3.5","3.5","5.6","5.6","5.6"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","1.7","1.7","1.7","2.7","2.7","2.7"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Operation range","Cooling","","Max.","°CDB","43","43","43","46.0","46.0","46.0"]
["","","","Min.","°CDB","10","10","10","10.0","10.0","10.0"]
["","Heating","","Max.","°CWB","25","25","25"]
["","","","Min.","°CWB","-20","-20","-20"]
["","Domestic hot water","","Min.","°CDB","-20","-20","-20","-20 (2)","-20 (2)","-20 (2)"]
["","","","Max.","°CDB","43","43","43","35 (2)","35 (2)","35 (2)"]
["Piping connections","Heat insulation","","","","","","","Both liquid and gas pipes","Both liquid and gas pipes","Both liquid and gas pipes"]
["","Liquid","","OD","mm","6.35","6.35","6.35","9.52","9.52","9.52"]
["","Gas","","OD","mm","15.9","15.9","15.9","15.90","15.90","15.90"]
["","Drain","","OD","mm","18","18","18","26","26","26"]
["","Level difference","IU - IU","Max.","m","20","20","20"]
["","","IU - OU","Max.","m","","","","30.0","30.0","30.0"]
["Sound power level","Heating","","Nom.","dBA","61","61","62","64 (3)","64 (3)","66 (3)"]
["","Cooling","","Nom.","dBA","63","63","63","64 (4)","66 (4)","69 (4)"]
["Dimensions","Unit","","Width","mm","825","825","825","900","900","900"]
["","","","Depth","mm","300","300","300","320","320","320"]
["","","","Height","mm","735","735","735","1,170","1,170","1,170"]
["Weight","Unit","","","kg","56","56","56","102","102","102"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Name","","","","V3","V3","V3","V3","V3","V3"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230"]
["Current","Recommended fuses","","","A","20","20","20","32","32","32"]
["Notes","","","","","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - See separate drawing for operation range","(1) - Operation range heating (outdoor unit): range increase by support back-up heater. See separate drawing for operation range.","(1) - Operation range heating (outdoor unit): range increase by support back-up heater. See separate drawing for operation range.","(1) - Operation range heating (outdoor unit): range increase by support back-up heater. See separate drawing for operation range."]
["","","","","","(2) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(2) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(2) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(2) - Operation range domestic hot water (outdoor unit): range increase by support booster heater or backup heater. See separate drawing for operation range.","(2) - Operation range domestic hot water (outdoor unit): range increase by support booster heater or backup heater. See separate drawing for operation range.","(2) - Operation range domestic hot water (outdoor unit): range increase by support booster heater or backup heater. See separate drawing for operation range."]
["","","","","","(3) - Minimum Ssc value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase","(3) - Minimum Ssc value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase","(3) - Minimum Ssc value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Contains fluorinated greenhouse gases","(4) - Contains fluorinated greenhouse gases","(4) - Contains fluorinated greenhouse gases","(4) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(4) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(4) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","","","","(5) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta DB/WB 7°C/6°C - LWC 3","(5) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta DB/WB 7°C/6°C - LWC 3","(5) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta DB/WB 7°C/6°C - LWC 3"]
["","","","","","","","","(6) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta 35°C - LWE 7°C ( DT =","(6) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta 35°C - LWE 7°C ( DT =","(6) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta 35°C - LWE 7°C ( DT ="]
["","","","","","","","","(7) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(7) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(7) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information."]
["","","","","","","","","(8) - Contains fluorinated greenhouse gases","(8) - Contains fluorinated greenhouse gases","(8) - Contains fluorinated greenhouse gases"]