{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":40,"n_cols":6,"rows_kept":40,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ERHQ-BW17"]
[]
[]
[]
[]
["","","","","","ERHQ014BAW17"]
["Sound pressure level","Heating","","Nom.","dBA","50 (6)"]
["","Cooling","","Nom.","dBA","50 (7)"]
["Sound power level","Heating","","Nom.","dBA","60 (4)"]
["","Cooling","","Nom.","dBA","66.0 (5)"]
["Refrigerant","Charge","","","kg","2.95"]
["","Type","","","","R-410A"]
["Dimensions","Unit","","Width","mm","900"]
["","","","Depth","mm","320"]
["","","","Height","mm","1,350"]
["Weight","Unit","","","kg","108"]
["Operation range","Cooling","","Max.","°CDB","46.0"]
["","","","Min.","°CDB","10.0"]
["","Domestic hot water","","Min.","°CDB","-20 (3)"]
["","","","Max.","°CDB","35 (3)"]
["Piping connections","Heat insulation","","","","Both liquid and gas pipes"]
["","Liquid","","OD","mm","9.52"]
["","Gas","","OD","mm","15.9"]
["","Drain","","OD","mm","26"]
["","Level difference","IU - OU","Max.","m","30.0"]
["Power supply","Phase","","","","3N~"]
["","Name","","","","W1"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","400"]
["Current","Recommended fuses","","","A","20"]
["Notes","","","","","(1) - PED unit category: excluded from scope of PED due to article 1, item 3.6 of 97/23/EC"]
["","","","","","(2) - Operation range heating (outdoor unit): range increase by support back-up heater. See separate drawing for operation range."]
["","","","","","(3) - Operation range domestic hot water (outdoor unit): range increase by support booster heater or backup heater. See separate drawing for operation range."]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(5) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","(6) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta DB/WB 7°C/6°C - LWC 3"]
["","","","","","(7) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information. Condition: Ta 35°C - LWE 7°C ( DT ="]
["","","","","","(8) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information."]
["","","","","","(9) - Down to 3m with recharging of the outdoor unit. Please refer to the installation manual of the outdoor unit."]
["","","","","","(10) - Minimum Ssc value: Equipment complying with EN/IEC 61000-3-12: European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and ≤ 75A per phase"]