{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":28,"n_cols":6,"rows_kept":28,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FHQ-B / RXS-J"]
[]
[]
[]
[]
["","","","","FHQ35BVV1B / RXS35J2V1B","FHQ50BVV1B / RXS50J2V1B"]
["Cooling capacity","Min.","","kW","1.4","1.7"]
["","Max.","","kW","3.7","5.6"]
["","Nom.","","kW","3.4 (3)","5.0 (3)"]
["Piping connections","Liquid","OD","mm","6.35","6.35"]
["","Gas","OD","mm","9.5","12.7"]
["","Drain","OD","mm","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)"]
["Nominal efficiency","EER","","","3.24","2.73"]
["","Annual energy consumption","","kWh","525","915"]
["","COP","","","3.60","2.93"]
["","Energy labeling Directive","Cooling","","A","D"]
["","","Heating","","B","D"]
["Heating capacity","Nom.","","kW","4.0 (4)","6.0 (4)"]
["","Min.","","kW","1.2","1.7"]
["","Max.","","kW","5.0","7.0"]
["Notes","","","","(1) - Energy label: scale from A (most efficient) to G (less efficient)","(1) - Energy label: scale from A (most efficient) to G (less efficient)"]
["","","","","(2) - Annual energy consumption: based on average use of 500 running hours per year at full load (nominal conditions)","(2) - Annual energy consumption: based on average use of 500 running hours per year at full load (nominal conditions)"]
["","","","","(3) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB, 24°CWB; equivalent piping length: 5m","(3) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB, 24°CWB; equivalent piping length: 5m"]
["","","","","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m"]
["","","","","(5) - 220V","(5) - 220V"]
["","","","","(6) - 230V","(6) - 230V"]
["","","","","(7) - 240V","(7) - 240V"]
["","","","","(8) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load","(8) - Nominal efficiency: cooling at 35°/27° nominal load, heating at 7°/20° nominal load"]