{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":67,"n_cols":13,"rows_kept":67,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWE-DT"]
[]
[]
[]
[]
["","","","","","FWE03DATN5V1L","FWE04DATN5V1L","FWE05DATN5V1L","FWE06DATN5V1L","FWE07DATN5V1L","FWE08DATN5V1L","FWE10DATN5V1L","FWE11DATN5V1L"]
["Standard Accessories","Installation and operation manual","","","","1","1","1","1","1","1","1","1"]
["","Screw bag","","","","1","1","1","1","1","1","1","1"]
["","Drain receiver","","","","1","1","1","1","1","1","1","1"]
["Total sound power level","Low","","","dBA","32.0","33.0","32.0","30.0","31.0","31.0","38.0","40.0"]
["","Fan speed 1","","","dBA","33.0","33.0","33.0","30.0","31.0","31.0","38.0","40.0"]
["","Fan speed 6","","","dBA","","","","50.0","50.0","50.0","57.0","59.0"]
["","High","","","dBA","42.0","44.0","50.0","50.0","50.0","50.0","57.0","59.0"]
["Water flow","Cooling","","Low","l/h","219","218","238","225","324","423","457","500"]
["","","","Fan speed 1","l/h","219","218","238","225","324","423","457","500"]
["","","","Fan speed 6","l/h","","","","560","685","702","937","1,005"]
["","","","High","l/h","316","368","461","560","685","702","937","1,005"]
["","Heating","","Fan speed 1","l/h","136","134","147","133","199","259","296","324"]
["","","","Fan speed 6","l/h","","","","354","438","449","610","654"]
["","","","High","l/h","201","233","293","354","438","449","610","654"]
["","","","Low","l/h","136","134","147","133","199","259","296","324"]
["","Water pressure drop","Heating","Fan speed 1","kPa","3","2","1","2","1","1","4","4"]
["","","","High","kPa","5","4","5","3","6","5","12","14"]
["","","","Fan speed 6","kPa","","","","","6","5","12","14"]
["","","","Low","kPa","3","2","1","2","1","1","4","4"]
["","","Cooling","Fan speed 6","kPa","","","","10","19","20","32","36"]
["","","","High","kPa","12","11","15","10","19","20","32","36"]
["","","","Fan speed 1","kPa","7","4","4","2","2","10","8","10"]
["","","","Low","kPa","7","4","4","2","2","10","8","10"]
["Piping connections","Drain","","OD","mm","17.3","17.3","17.3","17.3","17.3","17.3","17.3","17.3"]
["","Water","","Inlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["","","","Outlet","","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\"","3/4\""]
["Power input","Fan speed 6","","","kW","","","","0.062","0.065","0.067","0.104","0.110"]
["","Fan speed 1","","","kW","0.03","0.03","0.03","0.04","0.04","0.03","0.03","0.03"]
["","High","","","kW","0.031","0.032","0.039","0.062","0.065","0.067","0.104","0.110"]
["","Low","","","kW","0.03","0.03","0.03","0.04","0.04","0.03","0.03","0.03"]
["Dimensions","Unit","","Width","mm","797","797","797","997","1,200","1,200","1,200","1,200"]
["","","","Depth","mm","610","610","610","610","610","610","610","610"]
["","","","Height","mm","200","200","200","200","200","200","200","200"]
["Casing","Colour","","","","Metal","Metal","Metal","Metal","Metal","Metal","Metal","Metal"]
["Fan","Available static pressure","","Fan speed 1","Pa","20","20","20","20","20","20","20","20"]
["","","","High","Pa","40","50","50","50","50","50","50","50"]
["","","","Fan speed 6","Pa","","","","50","50","50","50","50"]
["","","","Low","Pa","20","20","20","20","20","20","20","20"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Fan speed 6","kW","3.22","4.28","4.59","2.56","3.14","3.22","4.28","4.59"]
["","","","Low","kW","1.95","2.11","2.30","1.02","1.48","1.95","2.11","2.30"]
["","","","Fan speed 1","kW","1.95","2.11","2.30","1.02","1.48","1.95","2.11","2.30"]
["","","","High","kW","3.22","4.28","4.59","2.56","3.14","3.22","4.28","4.59"]
["","Total capacity 2-pipe","","Fan speed 6","kW","","","","3.12","3.83","3.92","5.22","5.60"]
["","","","Low","kW","1.22","1.21","1.33","1.24","1.80","2.38","2.57","2.81"]
["","","","High","kW","1.77","2.06","2.58","3.12","3.83","3.92","5.22","5.60"]
["","","","Fan speed 1","kW","1.22","1.21","1.33","1.24","1.80","2.38","2.57","2.81"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","2.28","2.65","3.33","4.03","4.98","5.11","6.92","7.43"]
["","","","Fan speed 6","kW","","","","4.03","4.98","5.11","6.93","7.43"]
["","","","Low","kW","1.55","1.53","1.67","1.52","2.26","2.94","3.36","3.68"]
["","","","Fan speed 1","kW","1.55","1.53","1.67","1.52","2.26","2.94","3.36","3.68"]
["Current input","High","","","A","0.01","0.01","0.02","0.03","0.02","0.02","0.04","0.05"]
["","Fan speed 6","","","A","","","","0.03","0.02","0.02","0.04","0.05"]
["","Low","","","A","0.01","0.01","0.01","0.02","0.02","0.02","0.01","0.03"]
["","Fan speed 1","","","A","0.01","0.01","0.01","0.02","0.02","0.02","0.01","0.03"]
["Power supply","Type","","","","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50","220-240 / 1 / 50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB"]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]