{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":59,"n_cols":11,"rows_kept":59,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQG-L7V1/LY1"]
[]
[]
[]
[]
["","","","","","RZQG71L7V1B","RZQG71L7Y1B9","RZQG100L7Y1B","RZQG100L7V1B","RZQG125L7V1B","RZQG125L7Y1B"]
["Sound pressure level","Heating","","Nom.","dBA","50","50","52","","53","53"]
["","Cooling","","Nom.","dBA","48","48","50","","51","51"]
["","Night quiet mode","","Level 1","dBA","43","43","45","","45","45"]
["Standard Accessories","Tie-wraps","","","","2","2","2","2","2","2"]
["","Installation manual","","","","1","1","1","1","1","1"]
["Refrigerant","Charge","","","TCO2Eq","6.1","6.1","8.4","","8.4","8.4"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","","2,087.5","2,087.5"]
["","Charge","","","kg","2.9","2.9","4.0","","4.0","4.0"]
["","Type","","","","R-410A","R-410A","R-410A","","R-410A","R-410A"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","9.52","","9.52","9.52"]
["","Piping length","OU - IU","Max.","m","50","50","75","","75","75"]
["","","System","Chargeless","m","30","30","30","","30","30"]
["","","","Equivalent","m","70","70","90","","90","90"]
["","Gas","","OD","mm","15.9","15.9","15.9","","15.9","15.9"]
["","Level difference","IU - IU","Max.","m","0.5","0.5","0.5","","0.5","0.5"]
["","","IU - OU","Max.","m","30.0","30.0","30.0","","30.0","30.0"]
["","Additional refrigerant charge","","","kg/m","See installation manual 4P302555-1","See installation manual 4P302555-1","See installation manual 4P302555-1","","See installation manual 4P302555-1","See installation manual 4P302555-1"]
["Sound power level","Cooling","","","dBA","64","64","66","","67","67"]
["Dimensions","Unit","","Width","mm","940","940","940","","940","940"]
["","","","Depth","mm","320","320","320","","320","320"]
["","","","Height","mm","990","990","1,430","","1,430","1,430"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Weight","Unit","","","kg","78","80","101","","102","101"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","20","16","20","","32","20"]
["Power supply","Phase","","","","1~","3N~","3N~","","1~","3N~"]
["","Frequency","","","Hz","50","50","50","","50","50"]
["","Voltage","","","V","220-240","380-415","380-415","","220-240","380-415"]
["Notes","","","","","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC"]
["","","","","","(2) - Equipment complying with EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(2) - 3 with re-charging","(2) - 3 with re-charging","","(2) - Equipment complying with EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(2) - 3 with re-charging"]
["","","","","","(3) - Short-circuit power","(3) - See separate drawing for electrical data","(3) - See separate drawing for electrical data","","(3) - Short-circuit power","(3) - See separate drawing for electrical data"]
["","","","","","(4) - See separate drawing for electrical data","(4) - Contains fluorinated greenhouse gases","(4) - Contains fluorinated greenhouse gases","","(4) - See separate drawing for electrical data","(4) - Contains fluorinated greenhouse gases"]
["","","","","","(5) - 3 with re-charging","","","","(5) - 3 with re-charging"]
["","","","","","(6) - Contains fluorinated greenhouse gases","","","","(6) - Contains fluorinated greenhouse gases"]
["Sound power level","Cooling","","","dBA","","","","66"]
["Dimensions","Unit","","Height","mm","","","","1430"]
["","","","Width","mm","","","","940"]
["","","","Depth","mm","","","","320"]
["Weight","Unit","","","kg","","","","102"]
["Operation range","Cooling","Ambient","Min.","°CDB","","","","-15.0"]
["","","","Max.","°CDB","","","","50.0"]
["","Heating","Ambient","Min.","°CWB","","","","-20.0"]
["","","","Max.","°CWB","","","","15.5"]
["Sound pressure level","Cooling","","Nom.","dBA","","","","50"]
["","Heating","","Nom.","dBA","","","","52"]
["","Night quiet mode","","Level 1","dBA","","","","45"]
["Refrigerant","Charge","","","kg","","","","4.0"]
["","Charge","","","tCO2Eq","","","","8.4"]
["","GWP","","","","","","","2087.5"]
["Piping connections","Piping length","OU - IU","Max.","m","","","","75"]
["","Level difference","IU - OU","Max.","m","","","","30.0"]
["","","IU - IU","Max.","m","","","","0.5"]
["Power supply","Frequency","","","Hz","","","","50"]
["Notes","","","","","","","","(5) - 3 with re-charging"]