{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":36,"n_cols":9,"rows_kept":36,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQG-LY1L"]
[]
[]
[]
[]
["","","","","","RZQG71L8Y1L","RZQG100L8Y1L","RZQG125L8Y1L","RZQG140L7Y1L"]
["Sound pressure level","Heating","","Nom.","dBA","50","52","53","53"]
["","Cooling","","Nom.","dBA","48","50","51","52"]
["","Night quiet mode","","Level 1","dBA","43","45","45","45"]
["Standard Accessories","Tie-wraps","","","","2","2","2","2"]
["","Installation manual","","","","1","1","1","1"]
["Refrigerant","Charge","","","TCO2Eq","6.10","8.40","8.40","8.40"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","2.9","4.0","4.0","4.0"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","9.52","9.52"]
["","Piping length","OU - IU","Max.","m","50","75","75","75"]
["","","System","Chargeless","m","30","30","30","30"]
["","","","Equivalent","m","70","90","90","90"]
["","Gas","","OD","mm","15.9","15.9","15.9","15.9"]
["","Level difference","IU - IU","Max.","m","0.5","0.5","0.5","0.5"]
["","","IU - OU","Max.","m","30.0","30.0","30.0","30.0"]
["","Additional refrigerant charge","","","kg/m","See installation manual","See installation manual","See installation manual","See installation manual"]
["Sound power level","Cooling","","","dBA","64","66","67","69"]
["Dimensions","Unit","","Width","mm","940","940","940","940"]
["","","","Depth","mm","320","320","320","320"]
["","","","Height","mm","990","1,430","1,430","1,430"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Weight","Unit","","","kg","80","101","101","101"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","25","25","25"]
["Power supply","Phase","","","","3N~","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415"]
["Notes","","","","","(1) - 3 with re-charging","(1) - 3 with re-charging","(1) - 3 with re-charging","(1) - 3 with re-charging"]
["","","","","","(2) - See separate drawings for electrical data","(2) - See separate drawings for electrical data","(2) - See separate drawings for electrical data","(2) - See separate drawings for electrical data"]
["","","","","","(3) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(3) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(3) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC","(3) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC"]