{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":64,"n_cols":10,"rows_kept":64,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQSG-LV1/LY1"]
[]
[]
[]
[]
["","","","","","RZQSG71L2V1B","RZQSG100L7V1B","RZQSG100L7Y1B9","RZQSG125L7Y1B9","RZQSG125L7V1B"]
["Sound pressure level","Heating","","Nom.","dBA","","","","58"]
["","Cooling","","Nom.","dBA","","","","54"]
["","Night quiet mode","","Level 1","dBA","","","","49"]
["Standard Accessories","Tie-wraps","","","","2","2","2","2","2"]
["","Installation manual","","","","1","1","1","1","1"]
["Refrigerant","Charge","","","TCO2Eq","","","","6.1"]
["","GWP","","","","","","","2,087.5"]
["","Charge","","","kg","","","","2.9"]
["","Type","","","","","","","R-410A"]
["Operation range","Cooling","Ambient","Max.","°CDB","","","","46.0"]
["","","","Min.","°CDB","","","","-5.0"]
["","Heating","Ambient","Max.","°CWB","","","","15.5"]
["","","","Min.","°CWB","","","","-15.0"]
["Piping connections","Liquid","","OD","mm","","","","9.52"]
["","Piping length","OU - IU","Max.","m","","","","50"]
["","","System","Chargeless","m","","","","30"]
["","","","Equivalent","m","","","","70"]
["","Gas","","OD","mm","","","","15.9"]
["","Level difference","IU - IU","Max.","m","","","","0.5"]
["","","IU - OU","Max.","m","","","","30.0"]
["","Additional refrigerant charge","","","kg/m","","","","See installation manual 4P302555-1"]
["Sound power level","Cooling","","","dBA","","","","70"]
["Dimensions","Unit","","Width","mm","","","","940"]
["","","","Depth","mm","","","","320"]
["","","","Height","mm","","","","990"]
["Compressor","Type","","","","","","","Hermetically sealed swing compressor"]
["Weight","Unit","","","kg","","","","82"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","","","","20"]
["Power supply","Phase","","","","","","","3N~"]
["","Frequency","","","Hz","","","","50"]
["","Voltage","","","V","","","","380-415"]
["Notes","","","","","","","","(1) - PED: assembly = category l : excluded from scope of PED due to article 1, item 3.6 of 97/23/EC"]
["","","","","","","","","(2) - See separate drawing for electrical data"]
["","","","","","","","","(3) - Contains fluorinated greenhouse gases"]
["Dimensions","Unit","","Height","mm","770","990","990","","990"]
["","","","Width","mm","900","940","940","","940"]
["","","","Depth","mm","320","320","320","","320"]
["Weight","Unit","","","kg","67","81","82","","81"]
["Operation range","Cooling","Ambient","Min.","°CDB","-5.0","-5.0","-5.0","","-5.0"]
["","","","Max.","°CDB","46","46.0","46.0","","46.0"]
["","Heating","Ambient","Min.","°CWB","-15","-15.0","-15.0","","-15.0"]
["","","","Max.","°CWB","15.5","15.5","15.5","","15.5"]
["Sound power level","Cooling","","","dBA","65","69","69","","70"]
["Sound pressure level","Cooling","","Nom.","dBA","49","53","53","","54"]
["","Heating","","Nom.","dBA","51","57","57","","58"]
["Refrigerant","Charge","","","kg","2.75","2.9","2.9","","2.9"]
["","GWP","","","","2087.5","2087.5","2087.5","","2087.5"]
["","Charge","","","tCO2Eq","5.7","6.1","6.1","","6.1"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","9.52","","9.52"]
["","Gas","","OD","mm","15.9","15.9","15.9","","15.9"]
["","Piping length","OU - IU","Max.","m","30","50","50","","50"]
["","","System","Equivalent","m","40","70","70","","70"]
["","","","Chargeless","m","30","30","30","","30"]
["","Level difference","IU - OU","Max.","m","15","30.0","30.0","","30.0"]
["","","IU - IU","Max.","m","0.5","0.5","0.5","","0.5"]
["Power supply","Frequency","","","Hz","50","50","50","","50"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","20","32","20","","32"]
["Sound pressure level","Night quiet mode","","Level 1","dBA","","","49"]